## Sheet1
Parameter | Address | words Count | Data Type | Unit | mode | Add unit
Phase to Phase Voltage: U12 | 776 | 2 | U16 | 100 | READ | V
Phase to Phase Voltage: U23 | 778 | 2 | U16 | 100 | READ | V
Phase to Phase Voltage: U31 | 780 | 2 | U16 | 100 | READ | V
Phase to Neutral voltage phase 1 | 782 | 2 | U16 | 100 | READ | V
Phase to Neutral voltage phase 2 | 784 | 2 | U16 | 100 | READ | V
Phase to Neutral voltage phase 3 | 786 | 2 | U16 | 1000 | READ | V
Phase 1 Current | 768 | 2 | U16 | 1000 | READ | A
Phase 2 Current | 770 | 2 | U16 | 1000 | READ | A
Phase 3 Current | 772 | 2 | U16 | 1000 | READ | A
Neutral current | 774 | 2 | U16 | 1000 | READ | A
Frequency | 788 | 2 | U16 | 100 | READ | HZ
Reactiva Power | 792 | 2 | S32 | 0.1 | READ | W
Active Power | 794 | 2 | S32 | 0.1 | READ | W
Active Power phase1 +/- | 798 | 2 | S32 | 0.1 | READ | W
Active Power phase2 +/- | 800 | 2 | S32 | 0.1 | READ | W
Active Power phase3+/- | 802 | 2 | S32 | 0.1 | READ | W
Reactive Power phase1 +/- | 804 | 2 | S32 | 0.1 | READ | W
Reactive Power phase2+/- | 806 | 2 | S32 | 0.1 | READ | W
Reactive Power phase3 +/- | 808 | 2 | S32 | 0.1 | READ | W
power factor : -: leadiing et + : lagging : PF | 796 | 2 | S32 | 1000 | READ
Power factor phase 1 -:leading and +: lagging | 816 | 2 | S32 | 1000 | READ
Power factor phase 2 -:leading and +: lagging | 818 | 2 | S32 | 1000 | READ
Power factor phase 3 -:leading and +: lagging | 820 | 2 | S32 | 1000 | READ
Current Transformer secondary | 514 | 1 | U16 | 1 | WRITE
Current Transformer secondary1 | 513 | 1 | U8 | 1 | READ
Voltage Transformer primary | 516 | 2 | U32 | 1 | WRITE
Current Transformer secondary (1 : NO,2: YES) | 515 | 1 | U8 | .. | READ